## Slide 1
Energy Storage System Metering Configuration
ITWG Discussion
January 31, 2018

## Slide 2: Background - VDER Tariff
Some Uncertainty on Energy Storage compensation in value stack
  “Energy Storage paired with electric generating equipment, only the non-storage generation can qualify for Alternative 2 compensation.” – one utility tariff
  Not same in all utility tariffs, DPS has clarified ES green electrons should be eligible for Alt 2
  Stand alone Storage being fast tracked for VDER eligibility
Notes: Con Ed Nov 2017 Tariff Rider R “Energy Storage paired with electric generating equipment, only the non-storage generation can qualify for Alternative 2 compensation.”

## Slide 3: Implications
Interim period of green/brown eligibility can lead to restrictive configurations
  Limiting invertor configuration (Limiting to DC coupled system)
  Preventing battery discharge to the grid
  Or not receiving appropriate value
  Compensation limits (i.e. don’t get alt 2)

## Slide 4: Implications
Restrictions reduce benefit and value
  Building application BTM Storage + PV:
    If the battery is precluded from discharging during times of injection (to avoid brown electrons) then system can’t shift the green energy to higher value periods (i.e. Alt 2)
    If can’t grid charge the battery then cannot address customer demand
    If separate service then no customer BTM benefits

## Slide 5: Implications
Restrictions reduce benefit and value
  Community Solar + Storage:
    Station power from the grid is likely necessary
    If the Battery is precluded from exporting power then cannot shift CDG output
    Battery may need to shift grid-source power to provide ancillary services (inverter configuration matters)
Notes: Consume grid power
Export
And not be force to be DC coupled.

## Slide 6: Steps to provide clarity
  Eligible generation shifted by energy storage can receive VDER Alt 2 Capacity
  Action should anticipate Standalone Energy Storage VDER
  Metering as a solution for making sure grid-sourced and green electrons are appropriately compensated (as opposed to restrictive configurations to prevent occurrence)
Notes: Instead of preventing – compensate appropriately

## Slide 7: Key Use Cases
  Community/Remote Solar + Storage – Alt 2 capacity for PV-sourced energy during summer and flexibility to operate with grid-sourced energy to provide other services i.e. ISO ancillary or DISP…
  BTM Solar + Storage - Alt 2 capacity for PV-sourced energy during summer and flexibility to use grid-sourced energy to manage demand or provide services (i.e. demand response)

## Slide 8
Utility
METER
METER
METER
Typical Configuration
Source: Demand Energy

## Slide 9
Single line example
Source: Stem

## Slide 10
Validate solar only charging
Track grid and solar charging
Meter output for future attribute tracking
Flexibility of Multi-meter Configuration

## Slide 11
Day | Timestamp | PV meter OUT (kWh) | ES meter IN (kWh) | Green Tag | Difference (abs val) | ES meter OUT (kWH)
1-Jun | 0 | 0 | 0 | 1 | 0 | 0
1-Jun | 1 | 0 | 0 | 1 | 0 | 0
1-Jun | 2 | 0 | 0 | 1 | 0 | 0
1-Jun | 3 | 0 | 0 | 1 | 0 | 0
1-Jun | 4 | 0 | 200 | 0 | 200 | 0
1-Jun | 5 | 0 | 0 | 1 | 0 | 0
1-Jun | 6 | 0 | 0 | 1 | 0 | 0
1-Jun | 7 | 4 | 4 | 1 | 0 | 0
1-Jun | 8 | 118 | 118 | 1 | 0 | 0
1-Jun | 9 | 321 | 371 | 0 | 50 | 0
1-Jun | 10 | 1571 | 1571 | 1 | 0 | 0
1-Jun | 11 | 1785 | 1736 | 0 | 0 | 0
1-Jun | 12 | 1848 | 0 | 1 | 0 | 0
1-Jun | 13 | 1757 | 0 | 1 | 0 | 0
1-Jun | 14 | 1498 | 0 | 1 | 0 | 800
1-Jun | 15 | 1004 | 0 | 1 | 0 | 800
1-Jun | 16 | 152 | 0 | 1 | 0 | 800
1-Jun | 17 | 0 | 0 | 1 | 0 | 800
1-Jun | 18 | 0 | 0 | 1 | 0 | 800
1-Jun | 19 | 0 | 0 | 1 | 0 | 0
1-Jun | 20 | 0 | 0 | 1 | 0 | 0
1-Jun | 21 | 0 | 0 | 1 | 0 | 0
1-Jun | 22 | 0 | 0 | 1 | 0 | 0
1-Jun | 23 | 0 | 0 | 1 | 0 | 0
 |  |  |  |  | ESS Output 2-7pm | 4000
 |  |  |  |  | Total Grid Charge | 250
 |  |  |  |  | kWh for Alt 2 | 3750
 |  |  |  |  | kWh for Alt 3 | 250
Tracking Grid-Sourced and Solar Electrons
Measured
Calculated
Interval data is collected from meters at both the PV and ESS terminals
Grid-sourced and green energy is tallied
Appropriate compensation is applied to each
Source: Borrego Solar
Notes: 1) Interval data is collected from meters at both the PV and ESS terminals 2) The PV output meter is compared with the ESS input meter. Time stamped kWh values that match are tagged as green electrons. ESS imports that do not match a PV export are tagged as grid-sourced electrons. 3) All grid-sourced electrons are tallied in column H. 4) The ES output meter is tallied in column I. 5) In row 27, the ES output between 2-7pm is tallied. 6) In row 29, the total grid-sourced electrons tracked are subtracted from the ES output between 2-7pm. 7) The remaining kWh exported between 2-7pm receives Alt 2 treatment 8) The total grid-sourced electrons receive Alt 3 treatment.

## Slide 12: Other Considerations
  Due to cost of metering would not want to require multiple meter configuration for small systems (residential, possibly small commercial)
  Creates more overhead for utilities in billing
  Device level and/or third party metering should be allowed
  Can be used to choose VDER tariff or Load reduction for a DER output (Policy decision, but technically feasible)
  Metering can apply to both AC and DC coupled systems

## Slide 13: Key Use Cases
  Community/Remote Solar + Storage – Alt 2 capacity for PV-sourced energy during summer and flexibility to operate with grid-sourced energy to provide other services i.e. ISO ancillary or DISP…
  BTM Solar + Storage - Alt 2 capacity for PV-sourced energy during summer and flexibility to use grid-sourced energy to manage demand or provide services (i.e. demand response)

## Slide 14: Discussion