## Slide 1
Interconnection Policy Working Group
September, 17th 2018

## Slide 2
Agenda
Con Edison’s Distribution System Overview
NY SIR Preliminary Screening Analysis
Technical Screen A
Proposed Technical Screen A1
Other considerations

## Slide 3: Electric Operations Overview Distribution
The distribution system supplies power to low voltage Network customers and Radial customers from area substations at the primary service voltage levels.
  Majority of customers receive low voltage service directly at the distribution system secondary voltage levels
  A small percentage of high voltage customers receive power at primary service voltage
64 Network Systems
Supply 87% of System Demand
Radial System
Supplies 13% of System Demand
Area Substation
Feeders
Transformers
4kV, 13kV,
27kV, or 33kV
480, 208, or 120 V

## Slide 4: Typical Network Grid
120/208 Volt
Secondary Network Grid
Primary Feeder
(13/27/33 kV)
A
B
C
D
E
Network Transformer
Network Protector
Substation Breakers
Area Substation
PV Customer
Standard Customer

## Slide 5: DG Implications: Network Grid Service
Export capability dependent upon multiple factors
  PV size vs service capacity
  Network loading
  Nearby transformer loading
Upgrades to service may require street work
  Localized underground
  Increased customer cost & timeline

## Slide 6: Spot or Isolated Network
120/208 Volt
Network Grid
Primary Feeder
(13/27/33 kV)
A
B
C
D
E
Network Transformer
Spot or Isolated
Network
Network Protector
Substation Breakers
Area Substation
PV Customer
Large Customer
Standard Customer

## Slide 7: DG Implications: Isolated/Spot Network
Opening of network protector(s) would result in power loss to customer
Cannot accept export without upgrades
Solutions to enable export across network protector relays
Additional interconnection costs to accept export

## Slide 8: DG Export Solutions for Network System
Anti-Pumping Protection (APP):
  Application: Network grid service
  Description: Modifications to nearby transformers’ relays
  Typical Cost: Up to $50K
Communications Aided Tripping (CAT):
  Application: Isolated/Spot Network
  Description: Modifications to impacted transformers’ relays and communication to customer inverters.
  Typical Cost: $70-100K

## Slide 9
NY SIR Preliminary Screening Analysis
The utility performs Preliminary Screening Analysis for applications above 50kW to 5MW
Appendix G details technical screens A through F
If proposed DG system passes all of the technical screens the utility provides the applicant permission to build

## Slide 10
Preliminary Screen A
Screen A: Is the PCC on a Networked Secondary System?
Does the proposed system connect to a secondary network system?
Technical Screen A fails all applicants if the “Proposed system is connected to a secondary network system”. This results in either supplemental screen or CESIR study if the project would like to proceed to construction phase
Con Edison has an extensive secondary network system resulting in many applications failing Screen A
Con Edison is proposing additional Screen A1 only for Con Edison’s service territory

## Slide 11
Preliminary Screen A 1

## Slide 12
2017 Projects Breakdown
98% of DG installations in CE territory are PV, 1% are CHP
65% PV projects entering in the queue in 2017 were below 150kW
81 cases that went through a CESIR study
  in 2017 indicated that:
  Out of the 81, only 64 were eligible for Screen A1 as 17 were overhead or new service.
  Out of the 64 eligible for Screen A1
    60% would have failed Screen A1
    40% would have passed Screen A1

## Slide 13
Internal Process to conduct Screen A 1
Example:
Address: 141 East 48th St, New York, NY
Structure Name: M9359
M&S Plate: 28-J
Proposed 100 kW PV System
Step 1: Find the associated structure that the PV system wants to connect to using our Internal Vision Maps

## Slide 14
Internal Process to conduct Screen A 1
141 East 48thSt

## Slide 15
Internal Process to conduct Screen A 1
Step 2: Determine the All Time Minimum Load using our PVL Maps

## Slide 16
Internal Process to conduct Screen A 1
Step 3: Compare if the proposed system inverter size (kW) is less than the Suggested Hosting Capacity

## Slide 17
Other considerations associated with Screen A1
As AMI rolls out across the service territory we may consider revising the methodology of this screen
Clusters of projects, as we have seen more recently would likely not be able to utilize screen A1 because they would all be exporting into the same area and thus would require further study.
The data in our PVL map tools are only as good as the frequency that they have been refreshed. We will need to coordinate this testing in accordance with the refresh rate.
Screen A1 can’t be used for projects needing new services