## Slide 1: Technical Submittal Requirements for DG Projects
March 28, 2018

## Slide 2: DETAIL DESIGN SUBMITTAL PROCESS
<number>
The following submittals are required for project developers to submit at different stages of the design and construction process to successfully deliver an Interconnection project and to avoid unnecessary delays.
To schedule an initial site visit (this will only occur after 25% upgrade payment is received or 100% for upgrades under $10,000) :
    Site plan showing customer Interface pole, Meter pole (if changed from CESIR)
    Generator info - Generator Manufacturer’s Specifications(if changed from CESIR).
    Updated Appendix B(if changed from CESIR).
    Single line (with PE stamp if required) with comments addressed from CESIR.
    Three line – Follow information for one line (with PE stamp) with comments addressed from CESIR.

## Slide 3: DETAIL DESIGN SUBMITTAL PROCESS
To start Utility design and create a final schedule (Post site visit):
  Pole arrangement drawings (PE stamped, first pole only at this point)
  Finalized locations of poles staked out
  Site Plan (no PE stamp yet)
<number>

## Slide 4: CONSTRUCTION STAGE SUBMITTAL PROCESS
To start customer design/construction review , the following must be received and approved by the utility if changes occurred due to the CESIR results :
  PE stamped site plan
  PE stamped single line
  PE stamped three line
  PE stamped AC/DC elementary (if required)
  PE stamped electrical assembly and profile drawings
  Relay settings (if required)
  Protective Device Coordination study
  Labeled equipment designations on drawings
  Detail cut sheets for all electrical equipment (transformer, grounding bank, recloser, fuses, switches, etc.)
<number>

## Slide 5: Technical Submittals
To begin Company equipment construction on Customer premise:
  Drivable surface (access road)
To schedule a Field Verification:
  Stamped and accepted final construction package
<number>

## Slide 6: Technical Submittals
To schedule a Witness test:
  Accepted Field Verification/Engineering Inspection
  Sequence of Operations (SOO) , Energization Plan (EP) , Testing and Commissioning Plan (TCP), Maintenance Plan (MP)
For Permission to Operate to be issued:
  Completed Witness test along with any necessary self certifications.
  As left settings for relays
<number>