## Slide 1: Monitoring & Control Working Group
December 19, 2018

## Slide 2: Monitoring & Control Overview
Interconnection Technical Working Group
Justification
  Monitoring and control (M&C) is required for situational awareness to ensure the safe and reliable operation of the distribution system.
  May be used for creating efficiencies in system usage.
  Supports of advanced applications defined in DSIP roadmaps creating benefits for DER and consumers.
Definitions
  Monitoring - refers to near real-time telemetry as well as the reporting of values such as voltage, kW, kVar, and power factor on the distribution system in near-real time.
  Basic Control - refers to remotely changing the status of the device (e.g. open or close a disconnect device).
  Advanced Control - can also be defined as operational control, or the ability to change the output and/or dispatch other advanced capabilities of device.
Requirements
  ITWG approved an requirements (Sept 2017)
  The Joint Utilities (JU) are currently investigating lower-cost M&C solutions for DER
  Future requirements pertaining to advanced control are out of the scope at this time

## Slide 3: Current M&C Requirements
DPS ITWG Page: http://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/def2bf0a236b946f85257f71006ac98e/$FILE/DPS%20Monitoring%20and%20Control%20Requirements%20for%20Solar%20PV%20Projects%20in%20NY.pdf

## Slide 4: M&C Status Update – December 2018
Interconnection Technical Working Group
As of July 2017 a number of lower cost M&C solutions were identified but not yet incorporated into demonstrations.
As of December 2018 several of the identified M&C solutions have been evaluated and deployed.
The Joint Utilities (JU) have since developed an internal technical working group of Subject Matter Expert’s (SME’s) focused on sharing the lessons learned for low-cost M&C solution. This group has met twice since October, 2018 and will reconvene for a third meeting in January, 2018.
There is no standardized solution and use cases will drive technology, design and cost:
  Monitoring only – measurement for Operations, planning, etc. (protection is separate from M&C).
  Monitoring and Control – includes monitoring only as well as a control function to isolate the DER.

## Slide 5: Monitoring and Control Total Cost Estimates – December 2018
Interconnection Technical Working Group
Year | Solution | Type (Monitoring / Control) | Equipment / Procurement Cost | Engineering, Installation and Commissioning Cost | Total Cost
2017 | Recloser | M&C | N/A | N/A | $70,833
2017 | SEL RTU Package | M&C | $14,569 | $27,051 | $41,621
2018 | Micatu Sensor w/ SEL-734B | M | $37,600 | $11,300 | $48,900
2018 | Qinetiq Linewatch | M | $14,000 | $11,000 | $25,000
2018 | SEL 734B w/ Lindsay Sensor | M | $9,000 | $6,000 | $15,000
2018 | PMI Boomerang | M | $2,000 | $4,000 | $6,000

## Slide 6: Other Updates
Interconnection Technical Working Group
Most utilities are requiring monitoring updates on a frequency between 1 minute and 5 minutes with some having the capability to report by exception capability.
In addition to the procurement and engineering cost reductions, the Joint Utilities are demonstrating various communication methods to help further reduce M&C costs (e.g. cell, radio, cloud, ICCP, Dispersive Technologies, etc.).
Monitoring data previously not available for many interconnections has proved to be incredibly useful for operations, planning, forecasting and troubleshooting events.
The Joint Utilities has expressed the need to establish an inverter to meter solution to industry groups.
The M&C group is evaluating the Common Smart Inverter Profile (CSIP), published by Sunspec and accepted by the California Public Utilities Commission (CPUC) as a mandatory requirement for inverters starting in February 2019, to address many of the low-cost M&C and security requirements.
The group continues to look for new and upcoming solutions enabled by recent advances in technology; e.g. smart meter communications.

## Slide 7: Future Efforts
Interconnection Technical Working Group
The JU recommends updating the M&C requirements for solar PV to apply to all DER.
The JU is also recommending requirements be extended to Energy Storage Systems (ESR). Since ESR’s have the ability to charge and discharge, thus doubling the impact to the interconnected system a lower threshold may be warranted.
As the internal JU low-cost M&C SMEs continue to pilot new innovate and low-cost solutions, further review of the M&C requirements for DER may become necessary.
Scan rates between 5 sec and 5 minutes are being discussed and is dependent on use of data. (NYISO Security, ADMS for feeder monitoring, etc.)

## Slide 8: Appendix

## Slide 9: Monitoring & Control Reference Diagram
Interconnection Technical Working Group

## Slide 10: Monitoring and Control Equipment Costs – December 2018
Interconnection Technical Working Group
 | Meter | NEMA Encl | Sensors | Modem (Comms) | RTU | Contactor/ CBkr | Cost Eq (Avg) | Source
Recloser (M&C) |  |  |  |  |  |  | $71K | JU
SEL RTU Pkg (M&C) |  |  | χ |  |  | χ | $15K* | ICF
Micatu Sensor w/ SEL-734B (M) |  |  |  |  |  | χ | $38K* | JU
Qinetiq Linewatch (M) |  | ∫ |  |  | χ | χ | $14K* | JU
PMI Boomerang (M) |  | ∫ | χ |  | χ | χ | $2K* | JU
*Application may require additional equipment e.g. metal-clad switchgear