## Slide 1: EPRI Technical Update Harmonizing Screening & CESIR Processes in NY
Tom Key Sr. Program Manager
Ben York
Sr. Engineer
Project Update
December 1, 2016

## Slide 2: Harmonizing CESIR Processes in NY: Issues and Opportunities
Issues with existing processes:
  Wide range of study formats, technical, narratives and lengths
  New screening options in SIR not fully implemented
  Queue challenges for utilities across NY varies a lot
Opportunities for more unified study approach.
  More consistent application and better definition of SIR screens with use.
  Find best practices out of current range of studies and reporting.
  Follow thru with initiatives on difficult technical areas, such as anti islanding, network connections, etc.
  Prepare for the changes in 1547

## Slide 3: Work for NYSERDA - Harmonizing Interconnection Practices in NY State
  Team/scope: EPRI, NYSERDA, DPS and NY utilities, with input from outside NY, to identify best practices/processes grid connection from technical reviews to screening (new SIR) and CESIR studies.
    Task 1 – Functional specification (completed in October).
    Task 2 – Review screening and CESIR processes to address consistency and alignment in light of evolving criteria, differences in distribution types, changing standards (new 1547), and technical issues such as islanding/3Vo protection (in progress)
  Task 3 – Develop unified approach on screening and CESIR (by end of January).
Task 4 – Test drive approach with utilities on specific problematic cases in NY (by end of March ’17)

## Slide 4: Background/Status on Screening and CESIRs
New and improved technical procedures and processing of applications (last two years).
New SIR screens (March ‘16), still evolving and will need better definition of the pass/fail criteria.
Interconnection functional specifications defined (Oct ’16)
Current CESIR study approaches and details among NY utilities still varies at lot.
Current initiatives such as unintended islanding (Nov ‘16 to Jan ‘17) expected to better define SIR screens
Changes in IEEE 1547 are coming (late ‘17) and will need to be considered in all future requirements

## Slide 5: Expected flow of NY Interconnection Approval Process
Assumptions: Initial review is manual and utility unique, screening is based on NY SIR (March 2016), impact studies are CESIRs and may lead to Risk of Islanding (ROI) studies.

## Slide 6: Objectives for Harmonizing Screening and CESIRs
New York’s Family of Interconnection Requests Greater than 50kW
“first pass”
“not so fast”
DTT 3V0 Recloser
Uncertain Treatment?
Passing
# Passing with Refined Screening Criteria
Subject to Detailed Study
Opportunities for Improvement
# Subject to Detailed Study
New Screening Methods
All three areas; screening, studies, and mitigations have headroom for new innovations and improvements.
Of the three, screening is likely be the most cost-effective opportunity.

## Slide 7: Review of steps applying SIR and lead to CESIRs
Road to CESIR per SIR | Typical Implementation of NY Utility
Step 2 - Determine scope/nature, assign POC, offer pre-application report “like FERC” ($750) | Provide description of site-related limits and to identify if there are particular concerns with the specific site
Step 3 - Review of submittals, viability | Confirm if application complete per SIR appendix F
Step 3 - DG equipment verification | Check equipment per SIR appendixes B and C
Step 4 – SIR Screens A-F and verify Section II | Provide Table of Limits/Results
Step 4 – Letter report on A-F | Show results and estimated cost to continue
Step 4 – Offer supplemental screening H-J option | Confirm willingness to pay ($2,500) and provide report
Step 4 – Commit to CESIR study scope and provide cost estimate for study ($5-20k)? | Provided based on SIR, screening results and/or utility- feeder specific standards or other
Step 6 – Part I of CESIR | Review/disclose impacts expected to utility system and that need to be studied in this application case
Step 6 – Part II of CESIR ( | Detailed review and explanation of proposed system compliance with criterion in the SIR

## Slide 8: CESIR Technical Analysis Areas Included in Studies
Identify Analytical Methods used | Ratios, shorthand calculations, distribution loadflow program
 | Power related overvoltage
Voltage Analysis/Predictions | Voltage step change
(SIR Screens E, F, G) | Imbalance voltage
 | Regulating Equpment Operations
Thermal (screen C) | Equipment Rating Exceeded
 | Demand Masking
 | Additional Fault Current
Protection (Screens E, then G, perhaps I, also Sandia method may be applied and sometimes ROI additional study) | Coordination
 | Anti-Islanding (vs. load on feeder section)
 | 3V0/Substation
 | Backfeed/Unidirectional Relaying
(Screen D) | GFO/Effective Grounding
Power Quality (Screen H) | Resonance Scan? (Harmonics)
 | Flicker prediction or contingency
 | Distortion contingency

## Slide 9: Can SIR screens help with CESIR Harmonization?
Determine if reverse power problems; for network, (currently in SIR, screen A) and for radial (screen E)
Tests for possibility of islanding (screens B, E)
Check for thermal overloads, local service (C) and feeder (G)
Check for fault-related overvoltage potential
    Coefficient of Grounding on low-side of xformer, (screen D)
    GFO, 3Vo on high-side of xformer (not covered in SIR?)
    Transformer connection compatibility (not covered in SIR?)
Check steady state voltage limit and step changes (screen F)
Confirm protection coordination, fault current compatibility, breaker reach, and device ratings (not covered in SIR?)
Notes: flicker and harmonics depend on site and may be better treated case by case (following new 1547)

## Slide 10: Options for Screening DER Connections
Ratio Methods
  Minimum Load to Generation Ratio
  Stiffness Factor, Fault Ratio Factor, and Ground Source Impedance Ratio
Shorthand Calculation Methods
  Primary overvoltage
  Primary voltage deviation
  Regulator voltage deviation
  Element fault current
  Sympathetic breaker tripping
  Breaker reduction of reach
Computer-aided analytical methods (islanding, protection)
Detailed CESIR and ROI Studies

## Slide 11
Initial Review Minimal technical review
Application for Interconnection
CESIR and special studies Technical analysis required
Fail
Pass
Pass
Interconnection Approved
Approved (with site specific requirements)
Circuit or site mitigation requirements likely
Screening Options Technical analysis required
Pass
Ratio Methods
Computer-aided analytical Methods
Fail, with study $$
Increased data needed and accuracy
Shorthand Calculation Methods

## Slide 12: Currently too many screening choices and uncertainty, e.g. for islanding concern in NY
NYSIR Preliminary, screen B, (certified equipment) screen E (<33% min load) Also, DG size capacity on line section (<50% & <15% loadP
National Grid’s ESB 756 supplemental document
Sandia Screening Guideline (67% of min load)
Supplemental screen G (< 100% on line section) and Passing G requires checking screen H (voltage quality) and screen I (“safety and reliability”)
No Worries

## Slide 13: Collaborative Efforts to Update the Sandia Guide to Assess Islanding Risk (Sand2012-1365)
  Team/Scope: EPRI, NYSERDA, SNLA, NREL and industry will revise and update the March 2013 version of assessment guide and screens.
  Objective: Address questions about how the criteria was derived, methods to apply it and what needs changing with new 1547 and higher penetration.
  Planned Document Updates
    Scope and application cases to rule out and needing study
    Rework the flow chart ratio methods
    Address future smart inverters, ADMS
    Mitigations options onboard and grid side mitigation options
    Load characteristics and substation-level considerations
  Results: by 3/31/2017

## Slide 14: Next Steps and Schedule: Updating Sandia screening method (Sand2012-1365, of March 2013)
Issues with existing method:
  Needs more justification for using 2/3 min-load as first screen.
  The 2/3 min-load conflicts with a number of current practices.
  Screens that follow min-load require a lot of to get data.
  Most utilities go from first screen to a risk of Islanding (ROI) study.
Opportunities and role of an updated methods.
  Clarify the assessment steps that reached a 2/3 min-load allowance
  Address different power factor settings and trip limits
  Address new voltage and frequency ride through requirement
  Update on alternative methods for both on board and utility controlled anti islanding measures.
  Describe how this industry practice may compliment utility specific

## Slide 15: Next steps (Dec 2016 – Mar 2017)
Better define SIR screens A- I (pass/fail?, emerging 1547 requirements) - Working with research staff, utility distribution engineers and other stakeholders
Develop/Coordinate NY CESIR reports template - combine REV objectives with utility best practices
Work with utilities – to identify and select a few active and problematic interconnection cases
Test drive screening criteria and CESIR scope/format in the relevant field cases

## Slide 16: Together…Shaping the Future of Electricity
Ben York and Tom Key
byork@epri.com
tkey@epri.com
Thanks for your input!