## Slide 1: IEEE P1547
Babak Enayati, PhD, PE
IEEE 1547 Vice Chair
National Grid, Waltham, MA
Office: 781-907-3242
September 27, 2017
IEEE P1547: Standard for Interconnection and Interoperability of Distributed Energy Resources (DER) with Associated Electric Power Systems Interfaces
Notes: Congratulations to the legislature and NYSERDA for the creation of the vehicle rebate

## Slide 2: Index
Major impacts of high penetration of DER on the electric power system
What is the IEEE 1547 standard?
Why is the standard being revised?
What are the major changes to the standard?
What are the impacts of the standard revisions on the DER interconnection process?
National Grid’s stance
Recommendations

## Slide 3: Grid Transformation
Traditional Electric Grid…
Power park
Hydrogen Storage
Industrial DG
Modern Electricity Choices …
Combined Heat and Power
PV
Wind Farms
Rooftop Photovoltaics
Remote Loads
Fuel Cells
Utility Scale

## Slide 4: Two major Impacts of high penetration of DER on the electric power system
Impact on bulk power system stability (ride through)
Avoid blackouts like what happened in Germany and to avoid system instability issues like recent 1.2GW of solar generation loss in the Western Interconnection
Impact on Distribution System protection and power quality

## Slide 5: IEEE 1547
Title: Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces.
Scope: This standard establishes criteria and requirements for interconnection of distributed energy resources (DER) with electric power systems (EPS), and associated interfaces.

## Slide 6: Why is the standard being revised?
No voltage regulation by the DER
It is a must trip standard (No ride through)
Power quality issues were not properly addressed
No interoperability
Major issues with the 2003 version of the standard:

## Slide 7: Voltage regulation and ride through requirements
The ride-through capability and performance is proposed to be mandatory in the new standard.
The voltage regulation capability is proposed to be mandatory but the performance is proposed to be at the utility’s discretion (The DER will provide this capability and the utility will decide to enable/disable it and choose the proper operating modes).

## Slide 8: How are MA utilities addressing the ride through concerns?
IEEE 1547 revision has been on the MA Technical Standards Review Group (TSRG) meeting agenda for the past two years!! (https://sites.google.com/site/massdgic/home/interconnection/technical-standards-review-group )
A subgroups under TSRG was formed to address the ride through challenges. Target: ride through will be mandated in MA starting Jan 1, 2018.
Utilities and ISO-NE are members of this subgroup.
MA TSRG working group has recently decided to expand the scope of the subgroup to address the voltage and frequency regulation implementation challenges as well.

## Slide 9: Tentatively agreed ride through settings for Solar installations in MA
Voltage range (% of Nominal) | Minimum Ride-through Time in seconds
V > 120 | N/A
110 < V ≤ 120 | 12 seconds
70 ≤ V < 88 | 2 seconds
50 ≤ V < 70 | 1 second
V < 50 | 1 second
Frequency range (Hz) | Operating Mode | Minimum time(s) (design criteria)
f > 62.0 | N/A | N/A
60.6 < f ≤ 62.0 | Mandatory Operation a | 299
58.5 ≤ f ≤ 60.6 | Continuous Operation | Infinite ( c)
57.0 ≤ f < 58.5 | Mandatory Operation b | 299
f < 57.0 | N/A | N/A

## Slide 10: Ride through implementation target in MA
Starting Jan 1, 2018,
all inverter based generation
must meet the IEEE 1547
Category III requirements.
The momentary cessation
addresses the distribution
system protection issues
UL-1741SA can certify the
inverters to meet ISO-NE’s
requested ride through capability
Category III inverters with no
other rotating generation on
The same circuit will not require
DTT (UL 1741SA testing will be
trusted)

## Slide 11: IEEE 1547 implementation in MA
The IEEE 1547 subgroup under MA TSRG will come up with a timeline to implement the IEEE 1547 standard in MA.
Voltage regulation
Frequency regulation
Power quality
Microgrids
The biggest challenge identified as of now is “modeling”.
Full implementation of IEEE 1547 will depend on the IEEE 1547.1 revision as well.

## Slide 12: Recommendations
NY ITWG working group should work closely with NY-ISO to resolve the potential ride through challenges for DER interconnections.
The approach and lessons learned in MA should be taken into consideration
NY ITWG should also work on the voltage regulation adoption challenges i. e. modeling, etc

## Slide 13
Thank you!
Questions?
http://grouper.ieee.org/groups/scc21/1547_revision/1547revision_index.html