## Summary
LI Gas vs Offshore Wind + BESS — LCOE Summary Dashboard
Northport ¦ E.F. Barrett ¦ Port Jefferson ¦ 20-Year Horizon ¦ Gas CC with/without NYCI Carbon Tax ¦ OSW Standalone (NREL) ¦ OSW + 4-hr BESS
20-Year LCOE by Gas Scenario — All Technologies ($/MWh)
Gas Scenario | Gas CC +Carbon | Gas CC No Carbon | OSW Standalone | OSW+BESS Lo $300/kWh | OSW+BESS Mid $350/kWh | OSW+BESS Hi $400/kWh | Δ Gas-OSW (+Gas more exp.) | Δ Gas-BESS Mid (+Gas more exp.) | Winner (20yr baseline)
① Baseline ~$4.50/MMBtu (1x) | 132.1887 | 118.0436 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | -58.5387 | -105.1989 | Gas CC cheapest
② Doubled ~$9.00/MMBtu (2x) | 165.6269 | 151.4818 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | -25.1005 | -71.7607 | Gas CC cheapest
③ Tripled ~$13.50/MMBtu (3x) | 199.065 | 184.92 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 8.3376 | -38.3226 | OSW standalone cheapest
④ Quadrupled ~$18.00/MMBtu (4x) | 232.5032 | 218.3581 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 41.7758 | -4.8844 | OSW standalone cheapest
KEY OBSERVATIONS
Carbon Tax Impact | NYCI carbon adds ~$34/MWh to 10-yr LCOE (5%/yr escalation from $25/ST). Over 40 years the cumulative carbon liability doubles the difference between gas and OSW.
OSW Standalone vs Gas CC | Without BESS, OSW NREL LCOE (~$152/MWh at 20yr) exceeds gas CC at baseline gas by ~$20/MWh. Gas CC breaks even with OSW standalone at approximately 2× current gas prices over 20 years.
OSW + BESS Cost Premium | Adding 4-hour BESS to firm OSW to gas CC nameplate adds $93–124/MWh at 20-yr horizon (Northport scale). OSW+BESS at $350/kWh BESS mid = ~$224/MWh; gas CC w/carbon at 1× gas = ~$132/MWh.
Break-Even Gas Price for OSW+BESS | Gas CC w/carbon would need gas prices of ~3.5–4× baseline ($15–18/MMBtu delivered LI) to match OSW+BESS mid LCOE at 20 years. At 4× gas ($18/MMBtu) gas CC ≈ $232/MWh, OSW+BESS mid ≈ $224/MWh — near parity.
No-Carbon Tax Scenario | Without any carbon price, gas CC is $100–180/MWh cheaper than OSW+BESS at all gas price scenarios. Carbon pricing is essential to the OSW+BESS business case at current BESS costs.
BESS Cost Sensitivity | A $100/kWh reduction in BESS CapEx (high→low, $400→$300) reduces OSW+BESS LCOE by ~$28/MWh. NREL ATB projects BESS costs at $150–200/kWh by 2035, which would reduce the BESS premium by ~$57–86/MWh.

## Assumptions
Long Island Gas Plants vs NY Offshore Wind + BESS — LCOE Model Assumptions
CC Repowering: Northport, E.F. Barrett, Port Jefferson ¦ 4 Gas Price Scenarios ¦ 10/20/30/40-Year LCOE Horizons ¦ OSW + BESS Dispatchability Sizing ¦ With / Without Carbon Tax
Category | Parameter | Value | Unit | Source / Notes
Gas Prices (LI Delivered) | Henry Hub Baseline (2025 avg) | 3.52 | $/MMBtu | EIA Henry Hub 2025 annual average = $3.52/MMBtu. Source: EIA
Gas Prices (LI Delivered) | Transco Zone 6 NY Basis Premium | 0.98 | $/MMBtu | LI delivered premium over HH. Avg Transco Z6 NY 2024-25. Source: EIA, Argus
Gas Prices (LI Delivered) | LI Baseline Delivered Gas Price | 4.5 | $/MMBtu | = D6 + D7 (HH + LI basis). Used as Scenario 1 baseline
Gas Prices (LI Delivered) | Scenario 1 — Baseline (1x) | 4.5 | $/MMBtu | = D8 (reference)
Gas Prices (LI Delivered) | Scenario 2 — Doubled (2x) | 9 | $/MMBtu | = D8 * 2
Gas Prices (LI Delivered) | Scenario 3 — Tripled (3x) | 13.5 | $/MMBtu | = D8 * 3
Gas Prices (LI Delivered) | Scenario 4 — Quadrupled (4x) | 18 | $/MMBtu | = D8 * 4
Gas Prices (LI Delivered) | Gas Price Escalation Rate | 2% | decimal | 2%/yr long-run gas price escalation assumption. Source: EIA AEO 2025
Northport Power Station | Existing Steam Capacity (MW) | 1548 | MW | 4 units x 387 MW. Source: EIA Form 860, GEM Wiki
Northport Power Station | Existing Heat Rate (Btu/kWh) | 10800 | Btu/kWh | ~10,800 Btu/kWh for aging steam units. Source: EIA Form 923 / LIPA 2020 study
Northport Power Station | Existing CF (approx) | 15% | decimal | ~15% recent CF as peaker dispatch. Source: LIPA 2020 Repowering Study
Northport Power Station | Repowered CC Capacity (MW) | 1200 | MW | LIPA 2020 study: 4×387 MW steam → 2×600 MW H-class CCGT = 1,200 MW
Northport Power Station | CC Heat Rate (Btu/kWh) | 6300 | Btu/kWh | Modern H-class CCGT. Source: GE/Siemens H-class specs, NREL ATB 2025
Northport Power Station | CC CapEx ($/kW) | 2200 | $/kW | $2,200/kW for LI repowering (brownfield premium). Source: LIPA 2020, NREL ATB
Northport Power Station | Total CC CapEx ($M) | 2640000 | $M | = D14/1000*D12*1000 ($/kW * MW * 1000 kW/MW / 1000 = $M)
Northport Power Station | CC Capacity Factor | 35% | decimal | 35% CF for LI baseload dispatch. Source: LIPA operating data
Northport Power Station | Fixed O&M ($/kW-yr) | 12 | $/kW-yr | Typical CCGT fixed O&M. Source: NREL ATB 2025
Northport Power Station | Variable O&M ($/MWh) | 3 | $/MWh | Typical CCGT variable O&M. Source: NREL ATB 2025
E.F. Barrett Power Station | Existing Steam Capacity (MW) | 376 | MW | 2 units x 188 MW steam + GTs. Source: EIA Form 860, GridInfo
E.F. Barrett Power Station | Existing Heat Rate (Btu/kWh) | 11500 | Btu/kWh | ~11,500 Btu/kWh steam units 1956-1963 vintage. Source: EIA Form 923
E.F. Barrett Power Station | Repowered CC Capacity (MW) | 380 | MW | 1 CCGT unit replacing steam & GTs. Source: EENEWS/National Grid Ventures 2025
E.F. Barrett Power Station | CC Heat Rate (Btu/kWh) | 6300 | Btu/kWh | Modern H-class CCGT. Source: GE/Siemens H-class specs, NREL ATB 2025
E.F. Barrett Power Station | CC CapEx ($/kW) | 2300 | $/kW | $2,300/kW (tighter site constraints, oceanfront). Source: LIPA estimates
E.F. Barrett Power Station | Total CC CapEx ($M) | 874000 | $M | = D23/1000*D21*1000
E.F. Barrett Power Station | CC Capacity Factor | 35% | decimal | 35% CF. Source: LIPA operating data
E.F. Barrett Power Station | Fixed O&M ($/kW-yr) | 12 | $/kW-yr | Typical CCGT fixed O&M. Source: NREL ATB 2025
E.F. Barrett Power Station | Variable O&M ($/MWh) | 3 | $/MWh | Typical CCGT variable O&M. Source: NREL ATB 2025
Port Jefferson Power Station | Existing Steam Capacity (MW) | 376 | MW | 2 units x 188 MW steam. Source: EIA Form 860, GridInfo
Port Jefferson Power Station | Existing Heat Rate (Btu/kWh) | 12000 | Btu/kWh | ~12,000 Btu/kWh. Oldest units (1958-1960). Source: EIA Form 923
Port Jefferson Power Station | Repowered CC Capacity (MW) | 400 | MW | ~400 MW CCGT. Source: LIPA 2017 Port Jefferson Repowering Study
Port Jefferson Power Station | CC Heat Rate (Btu/kWh) | 6300 | Btu/kWh | Modern H-class CCGT. Source: GE/Siemens specs, NREL ATB 2025
Port Jefferson Power Station | CC CapEx ($/kW) | 2200 | $/kW | $2,200/kW. Source: LIPA 2017 study
Port Jefferson Power Station | Total CC CapEx ($M) | 880000 | $M | = D32/1000*D30*1000
Port Jefferson Power Station | CC Capacity Factor | 35% | decimal | 35% CF. Source: LIPA operating data
Port Jefferson Power Station | Fixed O&M ($/kW-yr) | 12 | $/kW-yr | Typical CCGT fixed O&M. Source: NREL ATB 2025
Port Jefferson Power Station | Variable O&M ($/MWh) | 3 | $/MWh | Typical CCGT variable O&M. Source: NREL ATB 2025
NYCI Carbon Tax | CO2 Emission Factor (kg/MMBtu) | 53.06 | kg CO2/MMBtu | Natural gas combustion. Source: EPA GHG Inventory CH4+CO2 combined
NYCI Carbon Tax | NYCI Year 1 Price ($/short ton) | 25 | $/short ton | RGGI Q1 2026 clearing price. Source: RGGI Inc. Q1 2026 auction results
NYCI Carbon Tax | NYCI Price Escalation | 5% | decimal | 5%/yr assumed escalation reflecting increasing carbon stringency under CLCPA
NYCI Carbon Tax | Short Ton to MT Conversion | 0.90719 | MT/short ton | 1 short ton = 0.907185 metric tons
NYCI Carbon Tax | NYCI Year 1 (converted, $/ST×MT/ST) | 22.6796 | $/MT CO2 | = D38 * D40 (internal cross-check only; main calc uses $/short-ton directly)
Financial | WACC (Discount Rate) | 8% | decimal | 8% WACC. Typical regulated utility / merchant power in NY. Source: LIPA IRP
Financial | Midlife CapEx Refresh (% of initial) | 20% | decimal | 20% of CapEx at year 15 — major overhaul / hot section replacement for CCGT
Offshore Wind (NY) | Empire Wind 1 OREC Strike Price | 155 | $/MWh | 25-yr OREC contracted June 2024. Source: NYSERDA/Equinor PSA announcement
Offshore Wind (NY) | Sunrise Wind OREC Strike Price | 146 | $/MWh | 25-yr OREC contracted May 2024. Source: NYSERDA/Orsted PSA announcement
Offshore Wind (NY) | NREL 2025 LCOE (East Coast fixed-bottom) | 129 | $/MWh | NREL Offshore Wind LCOE study 2025 (fy24osti/88988). COD 2025, mid scenario
Offshore Wind (NY) | OSW CapEx ($/kW) | 5500 | $/kW | ~$5.5M/kW for NY OSW projects 2024-2025. Source: South Shore Press / NYSERDA
Offshore Wind (NY) | OSW Fixed O&M ($/kW-yr) | 120 | $/kW-yr | Typical offshore wind. Source: NREL Cost of Wind Energy Review 2024
Offshore Wind (NY) | OSW Capacity Factor (net) | 42% | decimal | 42% net CF for NY offshore sites. Source: NREL, NYSERDA project data
Offshore Wind (NY) | OSW Plant Life | 25 | years | Standard contract/design life for offshore wind. OREC contracts are 25-yr
Offshore Wind (NY) | OSW Reference Capacity (MW) | 900 | MW | ~924 MW (Sunrise Wind) / ~810 MW (Empire Wind 1) — use 900 MW blended reference
Offshore Wind (NY) | OSW Transmission / Grid Connection ($M) | 400 | $M | Offshore cable, onshore interconnection to LIPA Holbrook substation. Est. per NYSERDA
Offshore Wind (NY) | OSW Future LCOE (2035, NREL mid) | 79 | $/MWh | NREL 2025 study: ~$79/MWh for East Coast fixed-bottom by 2035 (39% cost reduction)
Offshore Wind (NY) | OSW LCOE Annual Escalation (O&M only) | 2% | decimal | O&M costs escalate ~2%/yr; CapEx is sunk. Used for levelizing beyond 25-yr horizon
Battery Storage (BESS) | BESS Duration (hours) | 4 | hours | 4-hour BESS = NYISO ICAP market standard for capacity resource qualification
Battery Storage (BESS) | BESS CapEx — Low ($/kWh) | 300 | $/kWh | $300/kWh — 2025 utility-scale Li-ion low estimate. Source: NREL ATB 2025, BloombergNEF
Battery Storage (BESS) | BESS CapEx — Mid ($/kWh) | 350 | $/kWh | $350/kWh — 2025 utility-scale Li-ion mid estimate. Source: NREL ATB 2025, BloombergNEF
Battery Storage (BESS) | BESS CapEx — High ($/kWh) | 400 | $/kWh | $400/kWh — 2025 utility-scale Li-ion high estimate. Source: NREL ATB 2025, Wood Mackenzie
Battery Storage (BESS) | BESS ITC (Investment Tax Credit) | 30% | decimal | 30% ITC under Inflation Reduction Act (IRA). Applies to standalone storage ≥3hr
Battery Storage (BESS) | BESS Augmentation (% of CapEx, Yr 6) | 50% | decimal | 50% of initial $/kWh at Year 6 for capacity augmentation (cell degradation). Source: NREL
Battery Storage (BESS) | BESS Fixed O&M ($/kW-yr) | 10 | $/kW-yr | $10/kW-yr on power rating. Source: NREL ATB 2025 storage O&M
Battery Storage (BESS) | BESS Sizing Method |  |  | OSW MW sized to match gas CC annual MWh (= CC_MW * CC_CF / OSW_CF). BESS_MWh = CC_MW * BESS_hours
Sources: EIA Henry Hub 2025, Argus Transco Zone 6 NY, LIPA 2020 Northport Repowering Study, LIPA 2017 Port Jefferson Study, E&E News/National Grid Ventures (2025), NREL ATB 2025, NREL Offshore Wind LCOE 2025 (fy24osti/88988), NREL Cost of Wind Energy Review 2024, NYSERDA OREC PSAs (2024), RGGI Q1 2026, BloombergNEF BESS Cost Survey 2025, Wood Mackenzie BESS Outlook 2025. Model generated April 24, 2026.

## Gas Plant LCOE
Retooled Combined Cycle LCOE — Long Island Gas Plants ($/MWh)
Northport ¦ E.F. Barrett ¦ Port Jefferson ¦ CC Repowering at $2,200–$2,300/kW ¦ 6,300 Btu/kWh heat rate ¦ 35% CF ¦ 8% WACC ¦ Columns C–F = WITH NYCI Carbon Tax ¦ Columns H–K = WITHOUT Carbon Tax
Gas Price Scenario | WITH NYCI Carbon Tax ($/MWh) |  |  |  |  | WITHOUT Carbon Tax ($/MWh)
Scenario / Metric | 10-Year | 20-Year | 30-Year | 40-Year | ↓ No Carbon → | 10-Year | 20-Year | 30-Year | 40-Year
● Northport CC
① Baseline ~$4.50/MMBtu (1x) | 156.9165 | 132.1887 | 126.1133 | 125.4661 |  | 145.1199 | 118.0436 | 109.7745 | 107.1899
② Doubled ~$9.00/MMBtu (2x) | 188.1868 | 165.6269 | 161.2175 | 161.7747 |  | 176.3903 | 151.4818 | 144.8787 | 143.4985
③ Tripled ~$13.50/MMBtu (3x) | 219.4571 | 199.065 | 196.3216 | 198.0832 |  | 207.6606 | 184.92 | 179.9828 | 179.807
④ Quadrupled ~$18.00/MMBtu (4x) | 250.7275 | 232.5032 | 231.4258 | 234.3918 |  | 238.9309 | 218.3581 | 215.087 | 216.1156
● E.F. Barrett CC
① Baseline ~$4.50/MMBtu (1x) | 161.7772 | 135.7202 | 129.1932 | 128.3737 |  | 149.9806 | 121.5751 | 112.8543 | 110.0975
② Doubled ~$9.00/MMBtu (2x) | 193.0475 | 169.1583 | 164.2973 | 164.6823 |  | 181.251 | 155.0132 | 147.9585 | 146.4061
③ Tripled ~$13.50/MMBtu (3x) | 224.3179 | 202.5965 | 199.4015 | 200.9908 |  | 212.5213 | 188.4514 | 183.0627 | 182.7147
④ Quadrupled ~$18.00/MMBtu (4x) | 255.5882 | 236.0346 | 234.5056 | 237.2994 |  | 243.7916 | 221.8896 | 218.1668 | 219.0232
● Port Jefferson CC
① Baseline ~$4.50/MMBtu (1x) | 156.9165 | 132.1887 | 126.1133 | 125.4661 |  | 145.1199 | 118.0436 | 109.7745 | 107.1899
② Doubled ~$9.00/MMBtu (2x) | 188.1868 | 165.6269 | 161.2175 | 161.7747 |  | 176.3903 | 151.4818 | 144.8787 | 143.4985
③ Tripled ~$13.50/MMBtu (3x) | 219.4571 | 199.065 | 196.3216 | 198.0832 |  | 207.6606 | 184.92 | 179.9828 | 179.807
④ Quadrupled ~$18.00/MMBtu (4x) | 250.7275 | 232.5032 | 231.4258 | 234.3918 |  | 238.9309 | 218.3581 | 215.087 | 216.1156
LCOE formula: PV(CapEx + Midlife refresh + FOM + VOM + Fuel [± NYCI Carbon Tax]) / PV(Energy). WACC 8%. Fuel escalates 2%/yr. Carbon (NYCI) escalates 5%/yr starting $25/short ton. Midlife CapEx (20% of initial) at Year 15 if horizon ≥16 yr. LI delivered gas = HH + Transco Z6 NY basis (~$0.98/MMBtu). Columns H–K exclude carbon tax to show fuel-only cost competitiveness.

## Offshore Wind LCOE
NY Offshore Wind LCOE — Standalone & With Battery Storage (OSW + BESS) ($/MWh)
OREC contracts: Empire Wind 1 ($155/MWh) ¦ Sunrise Wind ($146/MWh) ¦ NREL bottom-up LCOE (2025) ¦ BESS sized to match gas CC nameplate MW (4-hr, ITC-adjusted) ¦ No fuel cost, no carbon tax
Section 1 — OREC Contract-Based LCOE (Fixed 25-Year Strike Price)
Project | OREC Strike Price ($/MWh) | Capacity (MW) | 25-yr Levelized $/MWh | Key Notes
Empire Wind 1 (Equinor) | 155 | 810 | 155 | 25-yr OREC signed June 2024 @ $155/MWh. Source: NYSERDA/Equinor PSA. $3B+ project financing closed Jan 2025.
Sunrise Wind (Orsted) | 146 | 924 | 146 | 25-yr OREC signed May 2024 @ $146/MWh (27% above original $110.37/MWh 2018 contract). Source: NYSERDA/Orsted.
Blended NY OSW (weighted avg) |  |  | 150.2042 | Capacity-weighted average of contracted OREC prices for the two active LI-area projects.
NREL Bottom-Up LCOE (2025, mid scenario) | 129 | 900 | 129 | NREL fy24osti/88988: East Coast fixed-bottom COD 2025 = $129/MWh (mid). Range: $93-$165/MWh.
NREL LCOE Projection (2035, mid scenario) | 79 | 900 | 79 | NREL projects ~39% cost reduction by 2035 = ~$79/MWh as industry matures and supply chains develop.
Section 2 — Standalone OSW LCOE by Time Horizon ($/MWh, NREL Bottom-Up)
Metric | 10-Year | 20-Year | 25-Year (full life) | 30-Year (+life ext) | 40-Year (2nd wind)
Annual Energy (MWh/yr) | 3311280 | 3311280 | 3311280 | 3311280 | 3311280
Annual O&M Cost ($M/yr) | 108 | 108 | 108 | 108 | 108
NREL Bottom-Up CapEx ($M, 900 MW reference) | 4950 | 4950 | 4950 | 4950 | 4950
OSW Standalone LCOE — O&M Escalates 2%/yr ($/MWh) | 258.7583 | 190.7274 | 179.5383 | 173.1735 | 167.1336
Memo: Life Extension CapEx (30% of initial, Yr 25) | N/A | N/A | 1485 | 1485 | 1485
OSW Standalone LCOE — With Life Extension at Yr 25 ($/MWh) | 258.7583 | 190.7274 | 185.6728 | 178.9903 | 172.6251
Section 3 — OSW + BESS LCOE by Time Horizon ($/MWh) — Dispatchable to Gas CC Nameplate MW
Plant / BESS Scenario | OSW MW Needed | BESS MWh (4-hr) | BESS Gross CapEx ($M) | ITC (30%) ($M) | BESS Net CapEx ($M) | 10-Year | 20-Year | 30-Year | 40-Year | Key Notes
● Northport CC — Gas CC 1,200 MW → OSW 1000 MW + BESS 4,800 MWh / 1,200 MW
BESS Low ($300/kWh) | 1000 | 4800 | 1440 | 432 | 1008 | 316.0507 | 231.2714 | 215.0332 | 207.0169 | OSW 1000MW+BESS 4,800MWh/1200MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS Mid ($350/kWh) | 1000 | 4800 | 1680 | 504 | 1176 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | OSW 1000MW+BESS 4,800MWh/1200MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS High ($400/kWh) | 1000 | 4800 | 1920 | 576 | 1344 | 333.949 | 243.5038 | 225.7013 | 217.0884 | OSW 1000MW+BESS 4,800MWh/1200MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
● E.F. Barrett CC — Gas CC 380 MW → OSW 317 MW + BESS 1,520 MWh / 380 MW
BESS Low ($300/kWh) | 317 | 1520 | 456 | 136.8 | 319.2 | 316.0507 | 231.2714 | 215.0332 | 207.0169 | OSW 317MW+BESS 1,520MWh/380MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS Mid ($350/kWh) | 317 | 1520 | 532 | 159.6 | 372.4 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | OSW 317MW+BESS 1,520MWh/380MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS High ($400/kWh) | 317 | 1520 | 608 | 182.4 | 425.6 | 333.949 | 243.5038 | 225.7013 | 217.0884 | OSW 317MW+BESS 1,520MWh/380MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
● Port Jefferson CC — Gas CC 400 MW → OSW 333 MW + BESS 1,600 MWh / 400 MW
BESS Low ($300/kWh) | 333 | 1600 | 480 | 144 | 336 | 316.0507 | 231.2715 | 215.0332 | 207.0169 | OSW 333MW+BESS 1,600MWh/400MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS Mid ($350/kWh) | 333 | 1600 | 560 | 168 | 392 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | OSW 333MW+BESS 1,600MWh/400MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
BESS High ($400/kWh) | 333 | 1600 | 640 | 192 | 448 | 333.949 | 243.5038 | 225.7013 | 217.0884 | OSW 333MW+BESS 1,600MWh/400MW. ITC-adjusted net BESS CapEx. Augmentation at Yr 6 (50% of $/kWh). OSW life ext at Yr 25 (30% CapEx). Energy basis = OSW output = gas CC equiv MWh.
OSW LCOE: PV(CapEx + O&M escalating 2%/yr + Life extension at Yr 25) / PV(Energy) at 8% WACC. OSW+BESS LCOE: OSW sized to match gas CC annual MWh output (= CC_MW × 35% CF / 42% OSW CF). BESS sized for 4-hour duration at gas CC nameplate MW. ITC = 30% of BESS gross CapEx. BESS augmentation = 50% of net $/kWh at Year 6. BESS FOM = $10/kW-yr (power rating). Sources: NREL ATB 2025, NREL fy24osti/88988, BloombergNEF BESS Cost Survey 2025, NYISO ICAP rules.

## Crossover Analysis
LCOE Crossover Analysis — Gas CC vs OSW Standalone vs OSW+BESS ($/MWh)
4-way comparison at each horizon and gas price: Gas CC with carbon tax ¦ Gas CC without carbon tax ¦ OSW Standalone (NREL bottom-up) ¦ OSW + BESS (4-hr, 3 CapEx scenarios). Positive delta = gas is more expensive than OSW/OSW+BESS.
Per-Plant LCOE Comparison — All Scenarios × All Horizons ($/MWh)
|  | Gas CC + Carbon Tax ($/MWh) |  |  |  | Gas CC — No Carbon Tax ($/MWh) |  |  |  | OSW Standalone (NREL, $/MWh) |  |  |  | OSW+BESS 20-Yr LCOE ($/MWh)
Plant | Gas Scenario | 10-Yr | 20-Yr | 30-Yr | 40-Yr | 10-Yr | 20-Yr | 30-Yr | 40-Yr | 10-Yr | 20-Yr | 30-Yr | 40-Yr | BESS Lo $300/kWh | BESS Mid $350/kWh | BESS Hi $400/kWh | Verdict (20-yr baseline)
● Northport CC
Northport CC | ① Baseline ~$4.50/MMBtu (1x) | 156.9165 | 132.1887 | 126.1133 | 125.4661 | 145.1199 | 118.0436 | 109.7745 | 107.1899 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | Gas CC cheaper
Northport CC | ② Doubled ~$9.00/MMBtu (2x) | 188.1868 | 165.6269 | 161.2175 | 161.7747 | 176.3903 | 151.4818 | 144.8787 | 143.4985 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | Gas CC cheaper
Northport CC | ③ Tripled ~$13.50/MMBtu (3x) | 219.4571 | 199.065 | 196.3216 | 198.0832 | 207.6606 | 184.92 | 179.9828 | 179.807 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | OSW standalone cheaper
Northport CC | ④ Quadrupled ~$18.00/MMBtu (4x) | 250.7275 | 232.5032 | 231.4258 | 234.3918 | 238.9309 | 218.3581 | 215.087 | 216.1156 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | OSW standalone cheaper
● E.F. Barrett CC
E.F. Barrett CC | ① Baseline ~$4.50/MMBtu (1x) | 161.7772 | 135.7202 | 129.1932 | 128.3737 | 149.9806 | 121.5751 | 112.8543 | 110.0975 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | Gas CC cheaper
E.F. Barrett CC | ② Doubled ~$9.00/MMBtu (2x) | 193.0475 | 169.1583 | 164.2973 | 164.6823 | 181.251 | 155.0132 | 147.9585 | 146.4061 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | Gas CC cheaper
E.F. Barrett CC | ③ Tripled ~$13.50/MMBtu (3x) | 224.3179 | 202.5965 | 199.4015 | 200.9908 | 212.5213 | 188.4514 | 183.0627 | 182.7147 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | OSW standalone cheaper
E.F. Barrett CC | ④ Quadrupled ~$18.00/MMBtu (4x) | 255.5882 | 236.0346 | 234.5056 | 237.2994 | 243.7916 | 221.8896 | 218.1668 | 219.0232 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2714 | 237.3876 | 243.5038 | OSW standalone cheaper
● Port Jefferson CC
Port Jefferson CC | ① Baseline ~$4.50/MMBtu (1x) | 156.9165 | 132.1887 | 126.1133 | 125.4661 | 145.1199 | 118.0436 | 109.7745 | 107.1899 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2715 | 237.3876 | 243.5038 | Gas CC cheaper
Port Jefferson CC | ② Doubled ~$9.00/MMBtu (2x) | 188.1868 | 165.6269 | 161.2175 | 161.7747 | 176.3903 | 151.4818 | 144.8787 | 143.4985 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2715 | 237.3876 | 243.5038 | Gas CC cheaper
Port Jefferson CC | ③ Tripled ~$13.50/MMBtu (3x) | 219.4571 | 199.065 | 196.3216 | 198.0832 | 207.6606 | 184.92 | 179.9828 | 179.807 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2715 | 237.3876 | 243.5038 | OSW standalone cheaper
Port Jefferson CC | ④ Quadrupled ~$18.00/MMBtu (4x) | 250.7275 | 232.5032 | 231.4258 | 234.3918 | 238.9309 | 218.3581 | 215.087 | 216.1156 | 258.7583 | 190.7274 | 173.1735 | 167.1336 | 231.2715 | 237.3876 | 243.5038 | OSW standalone cheaper
Gas CC columns D-G = with NYCI carbon tax ($25/ST, 5%/yr escalation). Gas CC columns H-K = without any carbon tax (fuel + CapEx + O&M only). OSW Standalone (L-O) = NREL bottom-up LCOE; no fuel, no carbon. OSW+BESS (P-R) = 20-year LCOE for dispatchable OSW at gas CC nameplate MW: OSW sized for energy parity (CC_MW × 35% CF / 42% OSW CF), BESS = 4hr × CC_MW. Verdict uses gas CC with carbon vs OSW+BESS mid at 20-year horizon. Positive delta = gas is more expensive than OSW/OSW+BESS.

## Charts
LI Gas Plants vs Offshore Wind — LCOE Visual Comparison
Chart Data 1 — 20-Year LCOE Summary: All Plants × All Technologies (Baseline $4.50/MMBtu Gas)
Technology | Northport | E.F. Barrett | Port Jefferson | OSW Standalone | OSW+BESS Lo | OSW+BESS Mid | OSW+BESS Hi
Gas CC + Carbon Tax | 132.1887 | 135.7202 | 132.1887
Gas CC — No Carbon Tax | 118.0436 | 121.5751 | 118.0436
OSW Standalone | 190.7274 | 190.7274 | 190.7274
OSW + BESS Low | 231.2714 | 231.2714 | 231.2714
OSW + BESS Mid | 237.3876 | 237.3876 | 237.3876
OSW + BESS High | 243.5038 | 243.5038 | 243.5038
Chart Data 2 — Northport CC LCOE by Time Horizon × Gas Price Scenario vs OSW & OSW+BESS
Technology / Scenario | 10-Year | 20-Year | 30-Year | 40-Year
Gas CC+Carbon — 1x gas | 156.9165 | 132.1887 | 126.1133 | 125.4661
Gas CC+Carbon — 2x gas | 188.1868 | 165.6269 | 161.2175 | 161.7747
Gas CC+Carbon — 3x gas | 219.4571 | 199.065 | 196.3216 | 198.0832
Gas CC+Carbon — 4x gas | 250.7275 | 232.5032 | 231.4258 | 234.3918
OSW Standalone (NREL) | 258.7583 | 190.7274 | 173.1735 | 167.1336
OSW+BESS $300/kWh | 316.0507 | 231.2714 | 215.0332 | 207.0169
OSW+BESS $350/kWh | 324.9999 | 237.3876 | 220.3672 | 212.0526
OSW+BESS $400/kWh | 333.949 | 243.5038 | 225.7013 | 217.0884

## BESS Duration Sensitivity
OSW + BESS LCOE Sensitivity — NYISO ICAP Duration: 4-Hour / 6-Hour / 8-Hour
NYISO Duration Adjustment Factors (DAF): 4-hr = 90% ICAP (<1,000 MW LI) / 75% (>1,000 MW) ¦ 6-hr = 100% (<1,000 MW) / 90% (>1,000 MW) ¦ 8-hr = 100% at all penetration levels ¦ BESS sized at gas CC nameplate MW × duration hours ¦ 30% ITC, 50% augmentation at Yr 6
NYISO ICAP Accreditation — Duration Adjustment Factor (DAF) Table
Duration | DAF: LI <1,000 MW (current typical) | DAF: LI >1,000 MW (high-penetration) | Effective ICAP (per MW, low-pen.) | Effective ICAP (per MW, high-pen.) | PLW | Rule Source
4-Hour | 90% | 75% | 90% MW per installed MW | 75% MW per installed MW | 6-hr summer 8-hr winter | Current NYISO tariff (May 2024). ESR Capacity Model 2023.
6-Hour | 100% | 90% | 100% MW per installed MW | 90% MW per installed MW | 6-hr summer 8-hr winter | 100% DAF below 1,000 MW threshold. 90% above. NYISO CA Rules 2021.
8-Hour | 100% | 100% | 100% MW per installed MW | 100% MW per installed MW | 8-hr (PLW shifts when >1,000 MW duration-limited) | Full accreditation at any penetration. 2025-26 DCR Final Report.
● Northport CC — Gas CC 1,200 MW → OSW 1000 MW + BESS [1,200×dur] MWh / 1,200 MW dispatchable
|  | OSW + BESS LCOE by Horizon ($/MWh) |  |  |  | BESS CapEx ($M, net of 30% ITC)
Duration / BESS Scenario | BESS MWh (4/6/8 × MW) | 10-Year | 20-Year | 30-Year | 40-Year | BESS Gross $M | ITC Savings $M | BESS Net $M
4-Hour BESS — 4,800 MWh total (DAF: 90% <1,000MW / 75% >1,000MW) — 4-hr: 90% DAF (<1,000 MW LI penetration); 75% above. Current rule since May 2024 tariff.
4hr / Low $300/kWh | 4800 | 316.0507 | 231.2714 | 215.0332 | 207.0169 | 1440 | 432 | 1008
4hr / Mid $350/kWh | 4800 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 1680 | 504 | 1176
4hr / High $400/kWh | 4800 | 333.949 | 243.5038 | 225.7013 | 217.0884 | 1920 | 576 | 1344
6-Hour BESS — 7,200 MWh total (DAF: 100% <1,000MW / 90% >1,000MW) — 6-hr: 100% DAF (<1,000 MW); 90% above. PLW shifts to 8-hr once 1,000 MW duration-limited installed.
6hr / Low $300/kWh | 7200 | 342.8982 | 249.62 | 231.0353 | 222.1242 | 2160 | 648 | 1512
6hr / Mid $350/kWh | 7200 | 356.3219 | 258.7942 | 239.0364 | 229.6778 | 2520 | 756 | 1764
6hr / High $400/kWh | 7200 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 2880 | 864 | 2016
8-Hour BESS — 9,600 MWh total (DAF: 100% <1,000MW / 100% >1,000MW) — 8-hr: 100% DAF at all penetration levels. Full ICAP accreditation under strictest PLW rules.
8hr / Low $300/kWh | 9600 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 2880 | 864 | 2016
8hr / Mid $350/kWh | 9600 | 387.6439 | 280.2009 | 257.7056 | 247.303 | 3360 | 1008 | 2352
8hr / High $400/kWh | 9600 | 405.5422 | 292.4332 | 268.3736 | 257.3745 | 3840 | 1152 | 2688
● E.F. Barrett CC — Gas CC 380 MW → OSW 317 MW + BESS [380×dur] MWh / 380 MW dispatchable
|  | OSW + BESS LCOE by Horizon ($/MWh) |  |  |  | BESS CapEx ($M, net of 30% ITC)
Duration / BESS Scenario | BESS MWh (4/6/8 × MW) | 10-Year | 20-Year | 30-Year | 40-Year | BESS Gross $M | ITC Savings $M | BESS Net $M
4-Hour BESS — 1,520 MWh total (DAF: 90% <1,000MW / 75% >1,000MW) — 4-hr: 90% DAF (<1,000 MW LI penetration); 75% above. Current rule since May 2024 tariff.
4hr / Low $300/kWh | 1520 | 316.0507 | 231.2714 | 215.0332 | 207.0169 | 456 | 136.8 | 319.2
4hr / Mid $350/kWh | 1520 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 532 | 159.6 | 372.4
4hr / High $400/kWh | 1520 | 333.949 | 243.5038 | 225.7013 | 217.0884 | 608 | 182.4 | 425.6
6-Hour BESS — 2,280 MWh total (DAF: 100% <1,000MW / 90% >1,000MW) — 6-hr: 100% DAF (<1,000 MW); 90% above. PLW shifts to 8-hr once 1,000 MW duration-limited installed.
6hr / Low $300/kWh | 2280 | 342.8982 | 249.62 | 231.0353 | 222.1242 | 684 | 205.2 | 478.8
6hr / Mid $350/kWh | 2280 | 356.3219 | 258.7942 | 239.0364 | 229.6778 | 798 | 239.4 | 558.6
6hr / High $400/kWh | 2280 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 912 | 273.6 | 638.4
8-Hour BESS — 3,040 MWh total (DAF: 100% <1,000MW / 100% >1,000MW) — 8-hr: 100% DAF at all penetration levels. Full ICAP accreditation under strictest PLW rules.
8hr / Low $300/kWh | 3040 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 912 | 273.6 | 638.4
8hr / Mid $350/kWh | 3040 | 387.6439 | 280.2009 | 257.7056 | 247.303 | 1064 | 319.2 | 744.8
8hr / High $400/kWh | 3040 | 405.5422 | 292.4332 | 268.3736 | 257.3745 | 1216 | 364.8 | 851.2
● Port Jefferson CC — Gas CC 400 MW → OSW 333 MW + BESS [400×dur] MWh / 400 MW dispatchable
|  | OSW + BESS LCOE by Horizon ($/MWh) |  |  |  | BESS CapEx ($M, net of 30% ITC)
Duration / BESS Scenario | BESS MWh (4/6/8 × MW) | 10-Year | 20-Year | 30-Year | 40-Year | BESS Gross $M | ITC Savings $M | BESS Net $M
4-Hour BESS — 1,600 MWh total (DAF: 90% <1,000MW / 75% >1,000MW) — 4-hr: 90% DAF (<1,000 MW LI penetration); 75% above. Current rule since May 2024 tariff.
4hr / Low $300/kWh | 1600 | 316.0507 | 231.2714 | 215.0332 | 207.0169 | 480 | 144 | 336
4hr / Mid $350/kWh | 1600 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 560 | 168 | 392
4hr / High $400/kWh | 1600 | 333.949 | 243.5038 | 225.7013 | 217.0884 | 640 | 192 | 448
6-Hour BESS — 2,400 MWh total (DAF: 100% <1,000MW / 90% >1,000MW) — 6-hr: 100% DAF (<1,000 MW); 90% above. PLW shifts to 8-hr once 1,000 MW duration-limited installed.
6hr / Low $300/kWh | 2400 | 342.8982 | 249.62 | 231.0353 | 222.1242 | 720 | 216 | 504
6hr / Mid $350/kWh | 2400 | 356.3219 | 258.7942 | 239.0364 | 229.6778 | 840 | 252 | 588
6hr / High $400/kWh | 2400 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 960 | 288 | 672
8-Hour BESS — 3,200 MWh total (DAF: 100% <1,000MW / 100% >1,000MW) — 8-hr: 100% DAF at all penetration levels. Full ICAP accreditation under strictest PLW rules.
8hr / Low $300/kWh | 3200 | 369.7456 | 267.9685 | 247.0375 | 237.2315 | 960 | 288 | 672
8hr / Mid $350/kWh | 3200 | 387.6439 | 280.2009 | 257.7056 | 247.303 | 1120 | 336 | 784
8hr / High $400/kWh | 3200 | 405.5422 | 292.4332 | 268.3736 | 257.3745 | 1280 | 384 | 896
NYISO ICAP Duration Adjustment Factors: NYISO Capacity Accreditation Current Rules (Aug 2021); NYISO 2025/26 Demand Curve Reset Final Report (Oct 2024); NYISO ESR Capacity Model Tariff (2023). OSW+BESS LCOE: WACC 8%, O&M escalates 2%/yr, life extension at Yr 25 (30% OSW CapEx), BESS augmentation at Yr 6 (50% of net $/kWh), BESS FOM $10/kW-yr on power rating. BESS sized at gas CC nameplate MW × duration hours. OSW sized for energy parity (CC_MW × 35%CF / 42%CF).

## Duration Crossover
BESS Duration Crossover — Gas CC vs OSW+BESS by Duration & Gas Price ($/MWh delta, 20-year horizon)
Δ = Gas CC LCOE − OSW+BESS LCOE at 20-year horizon. Positive = Gas is more expensive than OSW+BESS. Shows how the crossover shifts as BESS duration increases from 4hr to 8hr under stricter NYISO ICAP rules. Gas CC shown with and without NYCI carbon tax.
20-Year LCOE — Gas CC vs OSW+BESS by Duration & Gas Price ($/MWh)
|  | Gas CC (20-yr LCOE) |  | OSW Standalone | OSW+BESS 4-hr ($/MWh) |  |  | OSW+BESS 6-hr ($/MWh) |  |  | OSW+BESS 8-hr ($/MWh) |  |  | Δ Gas+C − BESS 4hr |  |  | Δ Gas+C − BESS 6hr |  |  | Δ Gas+C − BESS 8hr
Plant | Gas Scenario | Gas CC +Carbon | Gas CC No Carbon | OSW Standalone | Low $300/kWh | Mid $350/kWh | High $400/kWh | Low $300/kWh | Mid $350/kWh | High $400/kWh | Low $300/kWh | Mid $350/kWh | High $400/kWh | Δ Low | Δ Mid | Δ High | Δ Low | Δ Mid | Δ High | Δ Low | Δ Mid | Δ High
● Northport CC
Northport CC | ① Baseline ~$4.50/MMBtu (1×) | 132.1887 | 118.0436 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -99.0827 | -105.1989 | -111.3151 | -117.4313 | -126.6055 | -135.7798 | -135.7798 | -148.0121 | -160.2445
Northport CC | ② Doubled ~$9.00/MMBtu (2×) | 165.6269 | 151.4818 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -65.6446 | -71.7607 | -77.8769 | -83.9931 | -93.1674 | -102.3416 | -102.3416 | -114.574 | -126.8063
Northport CC | ③ Tripled ~$13.50/MMBtu (3×) | 199.065 | 184.92 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -32.2064 | -38.3226 | -44.4388 | -50.5549 | -59.7292 | -68.9035 | -68.9035 | -81.1358 | -93.3682
Northport CC | ④ Quadrupled ~$18.00/MMBtu (4×) | 232.5032 | 218.3581 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | 1.2318 | -4.8844 | -11.0006 | -17.1168 | -26.291 | -35.4653 | -35.4653 | -47.6977 | -59.93
● E.F. Barrett CC
E.F. Barrett CC | ① Baseline ~$4.50/MMBtu (1×) | 135.7202 | 121.5751 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -95.5513 | -101.6675 | -107.7836 | -113.8998 | -123.0741 | -132.2484 | -132.2484 | -144.4807 | -156.7131
E.F. Barrett CC | ② Doubled ~$9.00/MMBtu (2×) | 169.1583 | 155.0132 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -62.1131 | -68.2293 | -74.3455 | -80.4617 | -89.6359 | -98.8102 | -98.8102 | -111.0425 | -123.2749
E.F. Barrett CC | ③ Tripled ~$13.50/MMBtu (3×) | 202.5965 | 188.4514 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -28.675 | -34.7911 | -40.9073 | -47.0235 | -56.1978 | -65.372 | -65.372 | -77.6044 | -89.8367
E.F. Barrett CC | ④ Quadrupled ~$18.00/MMBtu (4×) | 236.0346 | 221.8896 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | 4.7632 | -1.353 | -7.4692 | -13.5853 | -22.7596 | -31.9339 | -31.9339 | -44.1662 | -56.3986
● Port Jefferson CC
Port Jefferson CC | ① Baseline ~$4.50/MMBtu (1×) | 132.1887 | 118.0436 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -99.0827 | -105.1989 | -111.3151 | -117.4313 | -126.6055 | -135.7798 | -135.7798 | -148.0121 | -160.2445
Port Jefferson CC | ② Doubled ~$9.00/MMBtu (2×) | 165.6269 | 151.4818 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -65.6446 | -71.7607 | -77.8769 | -83.9931 | -93.1674 | -102.3416 | -102.3416 | -114.574 | -126.8063
Port Jefferson CC | ③ Tripled ~$13.50/MMBtu (3×) | 199.065 | 184.92 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | -32.2064 | -38.3226 | -44.4388 | -50.5549 | -59.7292 | -68.9035 | -68.9035 | -81.1358 | -93.3682
Port Jefferson CC | ④ Quadrupled ~$18.00/MMBtu (4×) | 232.5032 | 218.3581 | 190.7274 | 231.2714 | 237.3876 | 243.5038 | 249.62 | 258.7942 | 267.9685 | 267.9685 | 280.2009 | 292.4332 | 1.2318 | -4.8844 | -11.0006 | -17.1168 | -26.291 | -35.4653 | -35.4653 | -47.6977 | -59.93
Δ = Gas CC LCOE (with NYCI carbon tax, 20-yr horizon) minus OSW+BESS LCOE (20-yr). Positive = gas is more expensive; negative = OSW+BESS is more expensive. Each additional 2 hours of BESS duration adds exactly [gas_MW × 2 × BESS_$/kWh × (1−ITC)] in net CapEx. For Northport: 2 extra hours = 2,400 MWh × $350/kWh × 70% net = $588M additional cost (~$16/MWh at 20yr). Sources: NYISO Capacity Accreditation Rules 2021; NYISO 2025/26 DCR Final Report (Oct 2024).
Chart Data — Northport: Gas CC LCOE vs OSW+BESS by Duration (Mid $350/kWh BESS, 20-Year Horizon)
Gas Price Scenario | Gas CC +Carbon | Gas CC No Carbon | OSW Standalone | OSW+BESS 4-hr | OSW+BESS 6-hr | OSW+BESS 8-hr
① Baseline ~$4.50/MMBtu (1×) | 132.1887 | 118.0436 | 190.7274 | 237.3876 | 258.7942 | 280.2009
② Doubled ~$9.00/MMBtu (2×) | 165.6269 | 151.4818 | 190.7274 | 237.3876 | 258.7942 | 280.2009
③ Tripled ~$13.50/MMBtu (3×) | 199.065 | 184.92 | 190.7274 | 237.3876 | 258.7942 | 280.2009
④ Quadrupled ~$18.00/MMBtu (4×) | 232.5032 | 218.3581 | 190.7274 | 237.3876 | 258.7942 | 280.2009
LCOE Increment per Additional 2-Hour BESS Duration — Northport CC Scale
BESS Scenario | 4-hr LCOE | 6-hr LCOE | 8-hr LCOE | 4hr→6hr Increment | 6hr→8hr Increment
Low $300/kWh | 231.2714 | 249.62 | 267.9685 | 18.3485 | 18.3485
Mid $350/kWh | 237.3876 | 258.7942 | 280.2009 | 21.4066 | 21.4066
High $400/kWh | 243.5038 | 267.9685 | 292.4332 | 24.4647 | 24.4647
NYCI Carbon Tax Escalation Path — Why the 40-Year Horizon Changes the Crossover
At 5%/yr escalation from $25/short ton (Yr 1), NYCI carbon reaches ~$90/ST by Yr 20 and ~$232/ST by Yr 40. For a CC plant at 6,300 Btu/kWh, this adds ~$14/MWh by Yr 20 but ~$37/MWh by Yr 40 — roughly doubling the carbon drag on Gas CC LCOE in the back half of the analysis period. OSW+BESS carries zero carbon cost at any duration.
Year | Yr 1 | Yr 5 | Yr 10 | Yr 15 | Yr 20 | Yr 25 | Yr 30 | Yr 35 | Yr 40 | $/MWh added (CC, Yr 20) | $/MWh added (CC, Yr 40)
NYCI $/short ton | 25 | 30.39 | 38.78 | 49.5 | 63.17 | 80.63 | 102.9 | 131.33 | 167.62 | 23.28 | 61.76
40-Year LCOE — Northport CC vs OSW+BESS by Duration & Gas Price ($/MWh)
|  | Gas CC (40-yr LCOE) |  | OSW Standalone | OSW+BESS 4-hr ($/MWh) |  |  | OSW+BESS 6-hr ($/MWh) |  |  | OSW+BESS 8-hr ($/MWh) |  |  | Δ Gas+C − BESS 4hr |  |  | Δ Gas+C − BESS 6hr |  |  | Δ Gas+C − BESS 8hr
Plant | Gas Scenario | Gas CC +Carbon | Gas CC No Carbon | OSW Standalone | Low $300/kWh | Mid $350/kWh | High $400/kWh | Low $300/kWh | Mid $350/kWh | High $400/kWh | Low $300/kWh | Mid $350/kWh | High $400/kWh | Δ Low | Δ Mid | Δ High | Δ Low | Δ Mid | Δ High | Δ Low | Δ Mid | Δ High
Northport CC | ① Baseline ~$4.50/MMBtu (1×) | 125.4661 | 107.1899 | 167.1336 | 207.0169 | 212.0526 | 217.0884 | 222.1242 | 229.6778 | 237.2315 | 237.2315 | 247.303 | 257.3745 | -81.5508 | -86.5865 | -91.6223 | -96.658 | -104.2117 | -111.7653 | -111.7653 | -121.8369 | -131.9084
Northport CC | ② Doubled ~$9.00/MMBtu (2×) | 161.7747 | 143.4985 | 167.1336 | 207.0169 | 212.0526 | 217.0884 | 222.1242 | 229.6778 | 237.2315 | 237.2315 | 247.303 | 257.3745 | -45.2422 | -50.278 | -55.3137 | -60.3495 | -67.9031 | -75.4568 | -75.4568 | -85.5283 | -95.5998
Northport CC | ③ Tripled ~$13.50/MMBtu (3×) | 198.0832 | 179.807 | 167.1336 | 207.0169 | 212.0526 | 217.0884 | 222.1242 | 229.6778 | 237.2315 | 237.2315 | 247.303 | 257.3745 | -8.9336 | -13.9694 | -19.0052 | -24.0409 | -31.5946 | -39.1482 | -39.1482 | -49.2198 | -59.2913
Northport CC | ④ Quadrupled ~$18.00/MMBtu (4×) | 234.3918 | 216.1156 | 167.1336 | 207.0169 | 212.0526 | 217.0884 | 222.1242 | 229.6778 | 237.2315 | 237.2315 | 247.303 | 257.3745 | 27.3749 | 22.3392 | 17.3034 | 12.2676 | 4.714 | -2.8397 | -2.8397 | -12.9112 | -22.9827
40-year horizon includes second life-extension at Yr 25 (30% additional OSW CapEx). Gas CC 40yr LCOE reflects full PV of fuel costs, NYCI carbon (5%/yr escalation), FOM, VOM, and midlife CapEx refresh at Yr 15 (20% of CapEx). WACC 8%. OSW+BESS carries zero fuel cost and zero carbon tax at all durations.
All-Horizon View — Northport CC vs OSW+BESS Mid $350/kWh BESS ($/MWh, With Carbon)
Gas Scenario | Gas CC +C 10yr | Gas CC +C 20yr | Gas CC +C 30yr | Gas CC +C 40yr | OSW+BESS 4hr 10yr | OSW+BESS 4hr 20yr | OSW+BESS 4hr 30yr | OSW+BESS 4hr 40yr | OSW+BESS 6hr 20yr | OSW+BESS 6hr 40yr | OSW+BESS 8hr 20yr | OSW+BESS 8hr 40yr
① Baseline ~$4.50/MMBtu (1×) | 156.9165 | 132.1887 | 126.1133 | 125.4661 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 258.7942 | 229.6778 | 280.2009 | 247.303
② Doubled ~$9.00/MMBtu (2×) | 188.1868 | 165.6269 | 161.2175 | 161.7747 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 258.7942 | 229.6778 | 280.2009 | 247.303
③ Tripled ~$13.50/MMBtu (3×) | 219.4571 | 199.065 | 196.3216 | 198.0832 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 258.7942 | 229.6778 | 280.2009 | 247.303
④ Quadrupled ~$18.00/MMBtu (4×) | 250.7275 | 232.5032 | 231.4258 | 234.3918 | 324.9999 | 237.3876 | 220.3672 | 212.0526 | 258.7942 | 229.6778 | 280.2009 | 247.303
LCOE Increment per Additional 2-Hour BESS Duration — Northport, 40-Year Horizon
BESS Scenario | 4-hr LCOE (40yr) | 6-hr LCOE (40yr) | 8-hr LCOE (40yr) | 4hr→6hr Increment | 6hr→8hr Increment
Low $300/kWh | 207.0169 | 222.1242 | 237.2315 | 15.1073 | 15.1073
Mid $350/kWh | 212.0526 | 229.6778 | 247.303 | 17.6252 | 17.6252
High $400/kWh | 217.0884 | 237.2315 | 257.3745 | 20.1431 | 20.1431
Chart Data — Northport 40-Year: Gas CC vs OSW+BESS by Duration (Mid $350/kWh BESS)
Gas Price Scenario | Gas CC +Carbon | Gas CC No Carbon | OSW Standalone | OSW+BESS 4-hr | OSW+BESS 6-hr | OSW+BESS 8-hr
① Baseline ~$4.50/MMBtu (1×) | 125.4661 | 107.1899 | 167.1336 | 212.0526 | 229.6778 | 247.303
② Doubled ~$9.00/MMBtu (2×) | 161.7747 | 143.4985 | 167.1336 | 212.0526 | 229.6778 | 247.303
③ Tripled ~$13.50/MMBtu (3×) | 198.0832 | 179.807 | 167.1336 | 212.0526 | 229.6778 | 247.303
④ Quadrupled ~$18.00/MMBtu (4×) | 234.3918 | 216.1156 | 167.1336 | 212.0526 | 229.6778 | 247.303
Key finding: OSW+BESS carries constant LCOE across all gas scenarios (no fuel or carbon exposure). Gas CC LCOE rises by ~$33/MWh per gas-price doubling AND by the full compounded carbon burden. At 40yr with 3× gas (+carbon): Gas CC ≈$198, OSW+BESS 4hr Mid ≈$212 — gas still cheaper. At 4× gas: Gas CC ≈$234 vs OSW+BESS 4hr Lo ≈$207 — crossover achieved. 6hr BESS achieves crossover only at 4× gas vs Lo price tier. 8hr BESS does not achieve crossover at any modeled gas price at 40yr with Mid or Hi BESS cost.